## Generators
Gen 1, Gen 2 |  |  | Gen 1
Parameter | Name | Value | Parameter | Name | Value
- | Type of Machine | Round Rotor | V | Operating Voltage (pu) | 1.03
S | Rated Power | 900MVA | P | Operating Real Power (MW) | 700
n | Number of Poles | 2 | QL | Operating Inductive Reactive Power (MVAr) | 185
f | Frequency | 60Hz
V | Nominal Voltage | 20kV | Gen 2
Xd | D-axis Synchronous Reactance | 1.80 pu | Parameter | Name | Value
Xq | Q-axis Synchronous Reactance | 1.70 pu | V | Operating Voltage (pu) | 1.01
Xl | Leakage Reactance | 0.20 pu | P | Operating Real Power (MW) | 700
X'd | D-axis Transient Reactance | 0.30 pu | QL | Operating Inductive Reactive Power (MVAr) | 235
X'q | Q-axis Transient Reactance | 0.55 pu
X''d | D-axis Subtransient Reactance | 0.25 pu | Gen 4
X''q | Q-axis Subtransient Reactance | 0.25 pu | Parameter | Name | Value
Ra | Armature Resistance | 0.0025 pu | V | Operating Voltage (pu) | 1.01
T'd0 | Open-Circuit D-Axis Transient Time Constant | 8.00 s | P | Operating Real Power (MW) | 700
T'q0 | Open-Circuit Q-Axis Transient Time Constant | 0.40 s | QL | Operating Inductive Reactive Power (MVAr) | 202
T''d0 | Open-Circuit D-Axis Subransient Time Constant | 0.03 s
T''q0 | Open-Circuit Q-Axis Subtransient Time Constant | 0.05 s
H | Inertia Coefficient | 6.50 s
Gen 4
Parameter | Name | Value
- | Type of Machine | Round Rotor
S | Rated Power | 900MVA
n | Number of Poles | 2
f | Frequency | 60Hz
V | Nominal Voltage | 20kV
Xd | D-axis Synchronous Reactance | 1.80 pu
Xq | Q-axis Synchronous Reactance | 1.70 pu
Xl | Leakage Reactance | 0.20 pu
X'd | D-axis Transient Reactance | 0.30 pu
X'q | Q-axis Transient Reactance | 0.55 pu
X''d | D-axis Subtransient Reactance | 0.25 pu
X''q | Q-axis Subtransient Reactance | 0.25 pu
Ra | Armature Resistance | 0.0025 pu
T'd0 | Open-Circuit D-Axis Transient Time Constant | 8.00 s
T'q0 | Open-Circuit Q-Axis Transient Time Constant | 0.40 s
T''d0 | Open-Circuit D-Axis Subransient Time Constant | 0.03 s
T''q0 | Open-Circuit Q-Axis Subtransient Time Constant | 0.05 s
H | Inertia Coefficient | 6.175

## Control Systems
Turbine Controls (PID) Controller
Parameter | Name | Value
P | Proportional Gain | 1
N | Filter Coefficient | 100
I | Integral Gain | 2
D | Derivative Gain | 0.2
UL | Upper Limit (pu) | 0.99
LL | Lower Limit (pu) | 0.5
Excitation Controls
Parameter | Name | Value
Tr | Low-Pass Filter Time Constant (s) | 0.05
Ka | Regulator Gain | 20
Ta | Regulator Time Constant (s) | 0.055
Ke | Exciter Gain | 1
Te | Exciter Time Constant (s) | 0
Tb | Transient Gain Reduction b (s) | 0
Tc | Transient Gain Reduction c (s) | 0
Kf | Damping Filter Gain | 0.125
Tf | Damping Filter Time Constant (s) | 1.8
Efmin | Regulator Lower Limit (pu) | -10
Efmax | Regulator Upper Limit (pu) | 10
Kp | Regulator Gain | 0

## Transformers
T1, T2, T3, T4
Parameter | Name | Value
- | Type of Transformer | Two Winding
- | Connection | Yg/Yg
S | Rated Power | 900MVA
V1 | Primary Winding Voltage | 20kV
V2 | Secondary Winding Voltage | 230kV
R | Resistance | 0.00 pu
X | Reactance | 0.15 pu
L* | Inductance (pu) | 0.00039789
L1* | Inductance of Winding 1 (pu) | 0.00019894
L2* | Inductance of Winding 2 (pu) | 0.00019894
X=wL=(2*pi*f)*L
* Calculated Value

## Transmission Lines
TL56, TL1011
Parameter | Name | Value
R | Resistance (pu/km) | 0.0001
X | Reactance (pu/km) | 0.001
V | Voltage (kV) | 230
SB | Base Power (MVA) | 100
l | Length (km) | 25
ZB | Base Impedance (ohms) | 529
R* | Resistance (ohms) | 1.3225
X* | Reactance (ohms) | 13.225
L* | Inductance (henries) | 0.03508
*Calculated Value
TL67, TL910
Parameter | Name | Value
R | Resistance (pu/km) | 0.0001
X | Reactance (pu/km) | 0.001
V | Voltage (kV) | 230
SB | Base Power (MVA) | 100
l | Length (km) | 10
ZB | Base Impedance (ohms) | 529
R* | Resistance (ohms) | 0.529
X* | Reactance (ohms) | 5.29
L* | Inductance (henries) | 0.014032
*Calculated Value
TL78-1, TL78-2, TL89-1, TL89-2
Parameter | Name | Value
R | Resistance (pu/km) | 0.0001
X | Reactance (pu/km) | 0.001
V | Voltage (kV) | 230
SB | Base Power (MVA) | 100
l | Length (km) | 110
ZB | Base Impedance (ohms) | 529
R* | Resistance (ohms) | 5.819
X* | Reactance (ohms) | 58.19
L* | Inductance (henries) | 0.15435

## Loads
Load 7
Parameter | Name | Value
P | Real Power | 967MW
QL | Inductive Reactive Power | 100MVAr
QC | Capacitive Reactive Power | 0MVAr
Load 9
Parameter | Name | Value
P | Real Power | 1767MW
QL | Inductive Reactive Power | 100MVAr
QC | Capacitive Reactive Power | 0MVAr

## Cap Banks
Cap Bank 7
Parameter | Name | Value
P | Real Power | 0MW
QL | Inductive Reactive Power | 0MVAr
QC | Capacitive Reactive Power | 200MVAr
Cap Bank 9
Parameter | Name | Value
P | Real Power | 0MW
QL | Inductive Reactive Power | 0MVAr
QC | Capacitive Reactive Power | 350MVAr

## System Equivalent
Parameter | Name | Value
VB | Voltage Base (kV) | 20kV
V | Voltage (pu) | 1.03
R | Internal Resistance (ohm) | 0
L | Internal Inductance (henries) | 0